## TEPX-M1
Level of manifolding | 1
Statepoint | L [m] | OD [mm] | ID [mm] | Q [W] | Pipe roughness Ep (um) | Routing | Volume | Liquid volume (m^3) | Vapour volume(m^3) | heat load (kW) | ph heat load (kW)
Section number | 5 | Nbranches= | 1 | MLevel= | 0 |  |  | 0.00030762 | 0.00044872 | 1.8795 | 0.128
300 | 3.2841 | 12.7 | 10.2 |  | 20 |  | 0.00026835
Section number | 6 | Nbranches= | 1 | MLevel= | 0
400 | 1.2568 | 8 | 6 |  | 20 |  | 3.5535e-05
Section number | 8 | Nbranches= | 8 | MLevel= | 1 | [6 empty] | Section number in this diagram correspond to the ones in column B
410 | 0.7178 | 2.2 | 0.72 |  | 20 | TEPX 11 Top | 2.9225e-07
410 | 0.7178 | 2.2 | 0.72 |  | 20 | TEPX 11 Bottom | 2.9225e-07
410 | 0.7178 | 2.2 | 0.72 |  | 20 | TEPX 12 Top | 2.9225e-07
410 | 0.7178 | 2.2 | 0.72 |  | 20 | TEPX 12 Bottom | 2.9225e-07
410 | 0.72043 | 2.2 | 0.72 |  | 20 | TEPX 21 Top | 2.9332e-07
410 | 0.72043 | 2.2 | 0.72 |  | 20 | TEPX 21 Bottom | 2.9332e-07
410 | 0.72043 | 2.2 | 0.72 |  | 20 | TEPX 22 Top | 2.9332e-07
410 | 0.72043 | 2.2 | 0.72 |  | 20 | TEPX 22 Bottom | 2.9332e-07
Section number | 9 | Nbranches= | 8 | MLevel= | 1
420 | 0.05 | 2.3 | 2.1 | 16 | 20 | TEPX 11 Top | 1.7318e-07
420 | 0.05 | 2.3 | 2.1 | 16 | 20 | TEPX 11 Bottom | 1.7318e-07
420 | 0.05 | 2.3 | 2.1 | 16 | 20 | TEPX 12 Top | 1.7318e-07
420 | 0.05 | 2.3 | 2.1 | 16 | 20 | TEPX 12 Bottom | 1.7318e-07
420 | 0.05 | 2.3 | 2.1 | 16 | 20 | TEPX 21 Top | 1.7318e-07
420 | 0.05 | 2.3 | 2.1 | 16 | 20 | TEPX 21 Bottom | 1.7318e-07
420 | 0.05 | 2.3 | 2.1 | 16 | 20 | TEPX 22 Top | 1.7318e-07
420 | 0.05 | 2.3 | 2.1 | 16 | 20 | TEPX 22 Bottom | 1.7318e-07
Section number | 10 | Nbranches= | 8 | MLevel= | 1
430 | 1.15 | 2.3 | 2.1 | 16.25 | 20 | TEPX 11 Top | 3.9831e-06
430 | 1.15 | 2.3 | 2.1 | 16.25 | 20 | TEPX 11 Bottom | 3.9831e-06
430 | 1.15 | 2.3 | 2.1 | 16.25 | 20 | TEPX 12 Top | 3.9831e-06
430 | 1.15 | 2.3 | 2.1 | 16.25 | 20 | TEPX 12 Bottom | 3.9831e-06
430 | 0.95 | 2.3 | 2.1 | 16.25 | 20 | TEPX 21 Top | 3.2904e-06
430 | 0.95 | 2.3 | 2.1 | 16.25 | 20 | TEPX 21 Bottom | 3.2904e-06
430 | 0.95 | 2.3 | 2.1 | 16.25 | 20 | TEPX 22 Top | 3.2904e-06
430 | 0.95 | 2.3 | 2.1 | 16.25 | 20 | TEPX 22 Bottom | 3.2904e-06
Section number | 11 | Nbranches= | 8 | MLevel= | 1
500 | 1.881 | 2.3 | 2.1 | 234.9375 | 20 | TEPX 11 Top | 6.515e-06
500 | 1.888 | 2.3 | 2.1 | 234.9375 | 20 | TEPX 11 Bottom | 6.5393e-06
500 | 1.881 | 2.3 | 2.1 | 234.9375 | 20 | TEPX 12 Top | 6.515e-06
500 | 1.888 | 2.3 | 2.1 | 234.9375 | 20 | TEPX 12 Bottom | 6.5393e-06
500 | 1.881 | 2.3 | 2.1 | 234.9375 | 20 | TEPX 21 Top | 6.515e-06
500 | 1.888 | 2.3 | 2.1 | 234.9375 | 20 | TEPX 21 Bottom | 6.5393e-06
500 | 1.881 | 2.3 | 2.1 | 234.9375 | 20 | TEPX 22 Top | 6.515e-06
500 | 1.888 | 2.3 | 2.1 | 234.9375 | 20 | TEPX 22 Bottom | 6.5393e-06
Section number | 12 | Nbranches= | 8 | MLevel= | 1
600 | 1.15 | 3.5 | 3 |  | 20 | TEPX 11 Top | 8.1289e-06
600 | 1.15 | 3.5 | 3 |  | 20 | TEPX 11 Bottom | 8.1289e-06
600 | 1.15 | 3.5 | 3 |  | 20 | TEPX 12 Top | 8.1289e-06
600 | 1.15 | 3.5 | 3 |  | 20 | TEPX 12 Bottom | 8.1289e-06
600 | 0.95 | 3.5 | 3 |  | 20 | TEPX 21 Top | 6.7152e-06
600 | 0.95 | 3.5 | 3 |  | 20 | TEPX 21 Bottom | 6.7152e-06
600 | 0.95 | 3.5 | 3 |  | 20 | TEPX 22 Top | 6.7152e-06
600 | 0.95 | 3.5 | 3 |  | 20 | TEPX 22 Bottom | 6.7152e-06
Section number | 14 | Nbranches= | 1 | MLevel= | 0
700 | 1.1755 | 8 | 6 |  | 20 |  | 3.3236e-05
Section number | 15 | Nbranches= | 1 | MLevel= | 0
800 | 3.363 | 12.7 | 10.2 |  | 20 |  | 0.0002748
Power in section 9 is the contribution of preheaters according to the estimation in specification document
Power in section 10 is the contribution of cables+portcards
Power in section 11 is the end-of-life contribution of chip+module leakage